MassSave Crew Lead: Combustion Safety Testing Guide

Adapted from ANSI/BPI 1200-2017

(1)  OUTSIDE: Calibrate Personal CO Monitor, Combustion Analyzer.

- With monitors running, enter house, inspect 1 min per floor.  Smell for gas leaks.

(2)  IS IT SAFE?  Ambient CO action levels.

1-35 ppm CO   Call Lead Vendor. Notify resident, open windows & doors. Check sources.

36+  ppm CO     TERMINATE and EVACUATE everyone.  Outside: Call Lead Vendor.

(3)  Worst-Case Setup for Combustion Safety Tests: Natural Conditions

- FIREPLACE, WOOD STOVE: COLD. Close dampers, cover ashes with wet paper.

- OPEN DOORS TO ROOMS WITH:

  - Heating RETURN Vents, VENTED EXHAUST Fans, DRYER. Turn off.

- CLOSE ALL OTHER DOORS:

  - EXTERIOR: Doors and Windows, attic access. AS in WINTER.

  - INTERIOR: Rooms WITHOUT Return Vents, Vented Exhaust Fans, or Dryer.

  - Combustion Area Zone (CAZ) Doors: Shut Supply Vents in CAZ. Keep makeup air.

- TURN OFF:

  - Vented Exhaust Fans, and DRYER - check FILTER and exterior OUTLET.

  - KEEP OFF Central AC, Window AC (seal), whole-house fan. Ignore roof vent fans.

- TURN OFF ALL VENTED COMBUSTION APPLIANCES:

  - GAS Water Heater: Set to Pilot. Turn off if no pilot.

  - Heating System: Turn off at service switch. Don’t use thermostat for boilers.

  - Furnace FILTER - if dirty, replace or remove.

(4)  WORST-CASE CAZ PRESSURE    	   MANOMETER: INPUT in CAZ, REF to Outside

| # CAZ DOOR | # NATURAL (Baseline) # Everything Off # CAZ door closed | # TURN ON vented exhaust fans # & clothes dryer | # TURN ON # Furnace Air Handler |
| --- | --- | --- | --- |
| # CLOSED => | # 1. pa | # 2. pa | # 3. pa |
| # OPEN => | # no measurement | # CAZ DOOR OPEN => | # 4. pa |

- Keep house in “WORST-CASE”.  Setup with the most-negative pressure (1, 2, 3, or 4).

(5)  SPILLAGE w/Timer:  Do Spill #1,2,3 & CO #1,2	Spillage   (6) CO(O) @ 5-min

1. SMALLEST unit (Input BTU).  DHW 2-min spill limit.	pass / fail

- Keep all systems running until finished

2. Larger units, SHARED FLUE: warm 2-min, cold 5-min       pass / fail

- If the Air Handler should be on, wait for it to start

3. RE-TEST Spill at smallest: 2-min after the heater starts	 pass / fail    .

4. Test all other units: cold 5-min, warm 2-min			 pass / fail

(7)  SPILLAGE ACTION LEVELS							Annex D, p.40-41

| If spillage FAILS in worst-case and … | ACTION REQUIRED |
| --- | --- |
| the Air Handler is on, then … --> | cover filter slot, seal ducts starting with returns, then resolve duct imbalances. or recommend service. |
| the CAZ Door is closed, then … --> | recommend measures to increase the air connection between CAZ and house. |
| excess exhaust from fans, appliances, or a flue vent problem, but NOT from the position of the CAZ door, or air handler, then ... --> | verify enough combustion air: see ANSI Z223.1/ NFPA 54 (gas), or ANSI Z223.1/ NFPA 31 (oil). Recommend service by qualified professional. |

- IF SPILL FAILS: Retest spillage in natural conditions.

- IF SPILL & CO FAIL: Strongly advise - TURN OFF, Notify service by qualified professional.

(8)  CO LIMITS & ACTIONS for Combustion Appliances*	  		p.13, Table 1

- Central Heater, Dryer, wall furnace (DV)		 400 ppm  CO(O) Air Free

- Water Heater, room heater, wall furnace (BIV)	 200 ppm  CO(O) Air Free

- Oven, broiler. Sec. 7.9.7 p. 14				 225 ppm  CO As Measured

- Gas Log in a wood-burning fireplace 		 400 ppm  CO(O) Air Free in firebox

- Gas Fireplace, gas refrigerator	 		   25 ppm  CO As Measured, in vent

- IF CO FAILS: Notify service by a qualified professional. Annex D, Table D.1.B.

(9)  When finished: Reset everything: water heater, thermostat, dampers, registers, fans, etc.

(10)  OVEN SAFETY TESTING: Turn on an exhaust fan or open a window.			p.14

□ STOVETOP BURNERS: Check flame color for incomplete combustion.

□ OVEN: EMPTY, TURN ON to 500F, start a TIMER and monitor ambient CO in kitchen.

□ AT 5 MINUTES, test OVEN CO:					 See Chart.

If any tests fail, advise homeowner to have serviced by a qualified professional.